## Effluent Q-III
LIQUID EFFLUENT POLLUTANT LEVEL FOR THE QUARTER III (OCT-TO-DEC) , 2015
MONITORED VALUES in mg/lit.except pH
SL. NO | PARAMETERS | NO. OF OBS | MAX. | MIN. | AVG. | Limiting value for conc. (mg/l except for pH) | Quantum limit in Kg / 1000 MT of crude processed
[7 empty] | Actual | Standard
1 | pH | 92 | 8.5 | 6 | 7.1667 | 6-8.5 | - | -
2 | OIL & GREASE | 92 | 4.8 | 1.6 | 2.88 | 5 | 1.98 | 2
3 | SULPHIDE | 92 | <0.1 | <0.1 | <0.1 | 0.5 | 0.07 | 0.2
4 | PHENOL | 92 | 0.34 | 0.05 | 0.16333 | 0.35 | 0.11 | 0.14
5 | S. SOLID | 92 | 18.2 | 4.8 | 11.5667 | 20 | 7.95 | 8
6 | COD | 92 | 116 | 25 | 59.9667 | 125 | 41.2 | 50
7 | BOD3 | 92 | 14 | 8 | 8.1333 | 15 | 5.59 | 6
8 | CN | 92 | <0.02 | <0.02 | <0.02 | 0.2 | 0.01 | 0.08
9 | Ammonia as N | 3 |  |  | 1.77 | 15 | 1.22 | 6
10 | Cr (Hexavalent) | 3 |  |  | 0 | 0.1 | 0 | 0.04
11 | Cr (Total) | 3 |  |  | 0.049333 | 2 | 0.03 | 0.8
12 | Pb | 3 |  |  | 0.031333 | 0.1 | 0.022 | 0.04
13 | Zn | 3 |  |  | 0.067 | 5 | 0.05 | 2
14 | Ni | 3 |  |  | 0.06 | 1 | 0.04 | 0.4
15 | Cu | 3 |  |  | 0.059 | 1 | 0.041 | 0.4
16 | Benzene | 3 |  |  | 0.0011667 | 0.1 | 0.001 | 0.04
17 | Benzo (a)- Pyrene | 3 |  |  | 0.00053333 | 0.2 | 0.0004 | 0.08
18 | Hg | 3 |  |  | BDL | 0.01 | 0 | 0.004
19 | V | 3 |  |  | 0.0033 | 0.2 | 0.0023 | 0.8
20 | TKN | 3 |  |  | 1.9333 | 40 | 1.33 | 16
21 | P | 3 |  |  | 1.2 | 3 | 0.83 | 1.2
Limiting concentration of effluent is as per MoEF notification on standard vide GSR-186 (E)dated 18th March, 2008.
* BDL- Detectable Limit : 0.1 microgram/Litre. All the parameters are found to be within limit
* Parameters from 9 to 21 are monitored once in a month as per CPCB norms

## Effluent Q-IV
1. LIQUID EFFLUENT POLLUTANT LEVEL FOR THE QUARTER IV (JAN-MARCH'16),2015-16
MONITORED VALUES in mg/lit.except pH
SL. NO | PARAMETERS | NO. OF OBS | MAX. | MIN. | AVG. | Limiting value for conc. (mg/l except for pH) | Quantum limit in Kg / 1000 MT of crude processed
[7 empty] | Actual | Standard
1 | pH | 91 | 8.5 | 6 | 7 | 6-8.5 | - | - | 0.68752
2 | OIL & GREASE | 91 | 4.9 | 1.5 | 2.8967 | 5 | 1.99 | 2
3 | SULPHIDE | 91 | <0.1 | <0.1 | <0.1 | 0.5 | 0.07 | 0.2
4 | PHENOL | 91 | 0.34 | 0.05 | 0.14 | 0.35 | 0.1 | 0.14
5 | S. SOLID | 91 | 19 | 8.4 | 11.6333 | 20 | 8 | 8
6 | COD | 91 | 75.5 | 28.8 | 53.1 | 125 | 36.5 | 50
7 | BOD3 | 91 | 14 | 8 | 8.7333 | 15 | 6 | 6
8 | CN | 91 | <0.02 | <0.02 | <0.02 | 0.2 | 0.01 | 0.08
9 | Ammonia as N | 3 |  |  | 1.55 | 15 | 1.07 | 6
10 | Cr (Hexavalent) | 3 |  |  | 0 | 0.1 | 0 | 0.04
11 | Cr (Total) | 3 |  |  | 0.042 | 2 | 0.03 | 0.8
12 | Pb | 3 |  |  | 0.026333 | 0.1 | 0.018 | 0.04
13 | Zn | 3 |  |  | 0.050667 | 5 | 0.03 | 2
14 | Ni | 3 |  |  | 0.054667 | 1 | 0.04 | 0.4
15 | Cu | 3 |  |  | 0.048667 | 1 | 0.033 | 0.4
16 | Benzene | 3 |  |  | 0.031 | 0.1 | 0.021 | 0.04
17 | Benzo (a)- Pyrene | 3 |  |  | 0.053533 | 0.2 | 0.0368 | 0.08
18 | Hg | 3 |  |  | BDL | 0.01 | 0 | 0.004
19 | V | 3 |  |  | 0.081267 | 0.2 | 0.0559 | 0.8
20 | TKN | 3 |  |  | 2.2167 | 40 | 1.52 | 16
21 | P | 3 |  |  | 1.73 | 3 | 1.19 | 1.2
Limiting concentration of effluent is as per MoEF notification on standard vide GSR-186 (E)dated 18th March, 2008.
* BDL- Detectable Limit : 0.1 microgram/Litre. All the parameters are found to be within limit
* Parameters from 9 to 21 are monitored once in a month as per CPCB norms

## Stack Q-III
QUARTERLY PERFORMANCE REPORT W.R.T ENVIRONMENTAL ASPECT.
DURING QUARTER II (OCT-DEC),2015-16
Online Stack Analyser data
UNIT | FURNACE STACK | PARAMETER | OBSERVED VALUE |  | Limiting Concentration in mg/Nm3 | Remarks Limit conc. calculated using fuel type& quan. used during the period
CONC. (In mg/Nm3)
|  |  | MAX. | MIN.
CDU/VDU | FF-01/02 | SO2 | 268.56 | 56.55 | 401 | Stack with dual firing (FG:FO=79:21)
|  | NOX | 202.24 | 32.54 | 371
|  | CO (FF1) | 42.5 | 2.5 | 161
|  | CO (FF2) | 42.3 | 1.08
DCU | FF-01 | SO2 | 165.65 | 5.75 | 787 | Stack with dual firing (FG:FO=55:45)
|  | NOX | 176.5 | 13.7 | 395
HCU | FF-01/02 | SO2 | 48.4 | 2.9 | 50 | Stack with Gas firing
|  | NOX | 83.11 | 3.28 | 350
HCU | FF-03 | SO2 | 267 | 7.94 | 272 | Stack with dual firing (FG:FO=87:13)
|  | NOX | 101 | 22.8 | 363
H2U | FF-01 | SO2 | 49.3 | 2 | 50 | Stack with Gas firing
|  | NOX | 96.5 | 8.432 | 350
MS | FF-01 | SO2 | 48.6 | 6 | 50 | Stack with Gas firing
|  | NOX | 279.9 | 6.6 | 350
CPP HRSG |  | SO2 | 48.7 | 3.8 | 50 | Stack with dual firing (FG:NAP=100:00)
|  | NOX | 190.1 | 8.1 | 350
CPP UTILITY BOILER |  | SO2 | 187.9 | 37.4 | 492 | Stack with Dual firing (FG:FO=73:27)
|  | NOX | 201.2 | 17.3 | 377
* Limiting concentration of emission calculated as per MOEF new notification on standard vide GSR- 186 (E) dated 18th March, 2008. Emission level for all the stacks are found to be within limit

## Stack Q-IV
QUARTERLY PERFORMANCE REPORT W.R.T ENVIRONMENTAL ASPECT.
DURING QUARTER IV (JAN-MARCH'16),2015-16
Online Stack Analyser data
UNIT | FURNACE STACK | PARAMETER | OBSERVED VALUE |  | Limiting Concentration in mg/Nm3 | Remarks Limit conc. calculated using fuel type& quan. used during the period
CONC. (In mg/Nm3)
|  |  | MAX. | MIN.
CDU/VDU | FF-01/02 | SO2 | 262.75 | 62.3 | 384 | Stack with dual firing (FG:FO=80:20)
|  | NOX | 200.9 | 19.07 | 370
|  | CO (FF1) | 29.5 | 1.63 | 160
|  | CO (FF2) | 30.75 | 1.88
DCU | FF-01 | SO2 | 228.48 | 8.85 | 567 | Stack with dual firing (FG:FO=69:31)
|  | NOX | 117.6 | 14.32 | 381
HCU | FF-01/02 | SO2 | 44.8 | 1 | 50 | Stack with Gas firing
|  | NOX | 223.7 | 5.13 | 350
HCU | FF-03 | SO2 | 139.1 | 8.87 | 144 | Stack with dual firing (FG:FO=94:6)
|  | NOX | 96.5 | 12.9 | 356
H2U | FF-01 | SO2 | 50 | 2.28 | 50 | Stack with Gas firing
|  | NOX | 96.5 | 5.13 | 350
MS | FF-01 | SO2 | 44.5 | 1.25 | 50 | Stack with Gas firing
|  | NOX | 223.7 | 1.68 | 350
CPP HRSG |  | SO2 | 49.8 | 4.2 | 50 | Stack with dual firing (FG:NAP=100:00)
|  | NOX | 187.6 | 4.2 | 350
CPP UTILITY BOILER |  | SO2 | 185.8 | 8.2 | 938 | Stack with Dual firing (FG:FO=46:54)
|  | NOX | 178.4 | 2.5 | 404
* Limiting concentration of emission calculated as per MOEF new notification on standard vide GSR- 186 (E) dated 18th March, 2008. Emission level for all the stacks are found to be within limit

## AAQM Q-III
NUMALIGARH REFINERY LIMITED
QUARTERLY PERFORMANCE WITH RESPECT TO ENVIRONMENTAL ASPECTS
DURING QUARTER III ( OCT TO DEC), 2015-16
Ambient Air Quality Data
STATION | PARAMETER | STD | Unit | OBSERVATIONS
|  | NAAQS-2009 |  | MAX | MIN | AVG.
REFINERY (WATCH TOWER NO. 6) | SO2 | 80 (24 hr avg.) | μg/m3 | 18.2 | 9.8 | 13.4
| NO2 | 80 (24 hr avg.) | μg/m3 | 19.6 | 10.7 | 14.4
| O3 | 100 (8 hr avg.) | μg/m3 | 24.6 | BDL | 20.1333
| CO | 2.0 (8 hr.avg.) | mg/m3 | 0.24 | BDL | 0.2
| NH3 | 400 (24 hr.avg.) | μg/m3 | 24.6 | BDL | 19.4333
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 64.1.2 | 44.8 | 55.8667
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 38.8 | 18.8 | 28
| Benzene | 05 (Annual) | μg/m3 | BDL | BDL | BDL
| BaP | 01 (Annual) | ng/m3 | BDL | BDL | BDL
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.21 | BDL | 0.21
| As | 06 (Annual) | ng/m3 | BDL | BDL | BDL
| Ni | 20 (Annual) | ng/m3 | 0.28 | 0.21 | 0.2
ECO-PARK IN NRL TOWNSHIP | SO2 | 80 (24 hr avg.) | μg/m3 | 10.2 | 4.3 | 7.1
| NO2 | 80 (24 hr avg.) | μg/m3 | 34.6 | 15.3 | 25.9
| O3 | 100 (8 hr avg.) | μg/m3 | 51.2 | 19.6 | 24.3233
| CO | 2.0 (8 hr.avg.) | mg/m3 | 0.85 | 0.24 | 0.59667
| NH3 | 400 (24 hr.avg.) | μg/m3 | 25.5 | 11.7 | 18.54
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 87 | 45 | 44.8
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 50 | 25 | 35.3333
| Benzene | 05 (Annual) | μg/m3 | 3.25 | 2 | 2.0333
| BaP | 1.0 (Annual) | ng/m3 | BDL | BDL | BDL
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.06 | 0.02 | 0.033333
| As | 6.0 (Annual) | ng/m3 | 1 | BDL | 2.0333
| Ni | 20 (Annual) | ng/m3 | 12.7 | 4 | 8.1533
RAW WATER INTAKE | SO2 | 80 (24 hr avg.) | μg/m3 | 7.5 | 4.5 | 5.7667
| NO2 | 80 (24 hr avg.) | μg/m3 | 33.4 | 11.6 | 23.2
| O3 | 100 (8 hr avg.) | μg/m3 | 32.2 | 19.6 | 24.1667
| CO | 2.0 (8 hr.avg.) | mg/m3 | 0.68 | 0.15 | 9.9
| NH3 | 400 (24 hr.avg.) | μg/m3 | 26.2 | 10 | 16.3667
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 74 | 40 | 66.4667
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 40 | 18 | 28.5667
| Benzene | 05 (Annual) | μg/m3 | 3.25 | 2.08 | 2.1733
| BaP | 01 (Annual) | ng/m3 | BDL | BDL | 1.0067
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.02 | BDL | 0.036667
| As | 06 (Annual) | ng/m3 | 1 | BDL | 1
| Ni | 20 (Annual) | ng/m3 | 11.9 | BDL | 6.9667
NH-39 BYPASS | SO2 | 80 (24 hr avg.) | μg/m3 | 9.2 | 4 | 6.8
| NO2 | 80 (24 hr avg.) | μg/m3 | 38.5 | 20.2 | 27.2
| O3 | 100 (8 hr avg.) | μg/m3 | 41.2 | 19.6 | 28.1
| CO | 2.0 (8 hr.avg.) | mg/m3 | 0.77 | 0.21 | 0.47
| NH3 | 400 (24 hr.avg.) | μg/m3 | 24.6 | 10 | 19.3667
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 88 | 36 | 69.9
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 50 | 24 | 33.4333
| Benzene | 05 (Annual) | μg/m3 | 3.25 | 1 | 2.2533
| BaP | 1 | ng/m3 | BDL | BDL | BDL
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.06 | BDL | 0.03
| As | 6 | ng/m3 | 1 | BDL | 1
| Ni | 20 (Annual) | ng/m3 | 12.93 | 4.58 | 7.5067
KAZIRANGA WILDLIFE SANCTUARY AT AGARTOLI | SO2 | 80 (24 hr avg.) | μg/m3 | 6.6 | 4 | 4.9
| NO2 | 80 (24 hr avg.) | μg/m3 | 25.5 | 12 | 17.4667
| O3 | 100 (8 hr avg.) | μg/m3 | 24.6 | 10.8 | 22.4333
| CO | 2.0 (8 hr.avg.) | mg/m3 | 0.41 | 0.11 | 0.19
| NH3 | 400 (24 hr.avg.) | μg/m3 | 15.5 | 2.6 | 10.5233
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 88 | 33 | 44.9667
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 37 | 15 | 23.7333
| Benzene | 05 (Annual) | μg/m3 | 2.85 | BDL | 2.0933
| BaP | 1 | ng/m3 | BDL | BDL | BDL
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.02 | BDL | 0.02
| As | 6 | ng/m3 | 1 | BDL | 1
| Ni | 20 (Annual) | ng/m3 | 4 | BDL | 1.8733
BDL:Below Detection Level, All the parameters are found to be within limt

## AAQM Q-IV
NUMALIGARH REFINERY LIMITED
QUARTERLY PERFORMANCE WITH RESPECT TO ENVIRONMENTAL ASPECTS
DURING QUARTER IV ( JAN-MARCH'16), 2015-16
Ambient Air Quality Data
STATION | PARAMETER | STD | Unit | OBSERVATIONS
|  | NAAQS-2009 |  | MAX | MIN | AVG.
REFINERY (WATCH TOWER NO. 6) | SO2 | 80 (24 hr avg.) | μg/m3 | 9.2 | 4.2 | 5.9333
| NO2 | 80 (24 hr avg.) | μg/m3 | 32.3 | 18.5 | 23.2667
| O3 | 100 (8 hr avg.) | μg/m3 | 33.6 | 19.6 | 25.2333
| CO | 2.0 (8 hr.avg.) | mg/m3 | 0.72 | 0.25 | 0.44333
| NH3 | 400 (24 hr.avg.) | μg/m3 | 15.5 | 10.6 | 12.5
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 87 | 49 | 60.6667
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 51 | 26 | 36
| Benzene | 05 (Annual) | μg/m3 | 3.25 | 2.08 | 1.4767
| BaP | 01 (Annual) | ng/m3 | BDL | BDL | BDL
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.06 | BDL | 0.03
| As | 06 (Annual) | ng/m3 | 1 | BDL | BDL
| Ni | 20 (Annual) | ng/m3 | 12.86 | 0.21 | 7.92
ECO-PARK IN NRL TOWNSHIP | SO2 | 80 (24 hr avg.) | μg/m3 | 6 | 4 | 4.7
| NO2 | 80 (24 hr avg.) | μg/m3 | 26.5 | 14.3 | 20.5667
| O3 | 100 (8 hr avg.) | μg/m3 | 26.8 | 19.6 | 22.6
| CO | 2.0 (8 hr.avg.) | mg/m3 | 0.51 | 0.24 | 0.28
| NH3 | 400 (24 hr.avg.) | μg/m3 | 17.2 | 10 | 12.0333
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 66 | 33 | 51
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 35 | 20 | 26.3333
| Benzene | 05 (Annual) | μg/m3 | 2.08 | 2 | 2.0267
| BaP | 1.0 (Annual) | ng/m3 | BDL | BDL | BDL
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.03 | 0.02 | 0.02
| As | 6.0 (Annual) | ng/m3 | 1 | BDL | 1
| Ni | 20 (Annual) | ng/m3 | 7.25 | 4 | 4.6233
RAW WATER INTAKE | SO2 | 80 (24 hr avg.) | μg/m3 | 5.8 | 4 | 4.7533
| NO2 | 80 (24 hr avg.) | μg/m3 | 21.4 | 11.6 | 15.9667
| O3 | 100 (8 hr avg.) | μg/m3 | 27.3 | 19.6 | 21.3
| CO | 2.0 (8 hr.avg.) | mg/m3 | 0.28 | 0.13 | 0.19
| NH3 | 400 (24 hr.avg.) | μg/m3 | 12.5 | 10 | 10.5667
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 58 | 27 | 38.7
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 40 | 12 | 23.4333
| Benzene | 05 (Annual) | μg/m3 | 2.08 | 2 | 2.0533
| BaP | 01 (Annual) | ng/m3 | BDL | BDL | 1.0067
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.02 | BDL | 0.02
| As | 06 (Annual) | ng/m3 | 1 | BDL | 1
| Ni | 20 (Annual) | ng/m3 | 4 | BDL | 3.7333
NH-39 BYPASS | SO2 | 80 (24 hr avg.) | μg/m3 | 5.9 | 4.2 | 5.2
| NO2 | 80 (24 hr avg.) | μg/m3 | 26.5 | 13.7 | 20.0667
| O3 | 100 (8 hr avg.) | μg/m3 | 36.2 | 19 | 23.4667
| CO | 2.0 (8 hr.avg.) | mg/m3 | 0.58 | 0.39 | 0.39
| NH3 | 400 (24 hr.avg.) | μg/m3 | 16.9 | 10.3 | 12.4667
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 73 | 38 | 55.3333
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 36 | 20 | 28
| Benzene | 05 (Annual) | μg/m3 | 2.08 | 0.78 | 1.6233
| BaP | 1 | ng/m3 | BDL | BDL | BDL
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.03 | BDL | 0.02
| As | 6 | ng/m3 | 1 | BDL | 1
| Ni | 20 (Annual) | ng/m3 | 8.9 | BDL | 4.1333
KAZIRANGA WILDLIFE SANCTUARY AT AGARTOLI | SO2 | 80 (24 hr avg.) | μg/m3 | 5.7 | 4 | 4.5
| NO2 | 80 (24 hr avg.) | μg/m3 | 22.7 | 10.5 | 16.4
| O3 | 100 (8 hr avg.) | μg/m3 | 26.6 | 19 | 20.4667
| CO | 2.0 (8 hr.avg.) | mg/m3 | 0.24 | 0.11 | 0.17333
| NH3 | 400 (24 hr.avg.) | μg/m3 | 12.3 | 9.8 | 10.4033
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 43 | 26 | 32.3333
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 37 | 13 | 19.6667
| Benzene | 05 (Annual) | μg/m3 | 2.08 | BDL | 2
| BaP | 1 | ng/m3 | BDL | BDL | BDL
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.02 | BDL | 0.02
| As | 6 | ng/m3 | 1 | BDL | 1
| Ni | 20 (Annual) | ng/m3 | 4 | BDL | 2.2333
BDL:Below Detection Level, All the parameters are found to be within limt