## PAHARPUR 01
Annexure -II
Tender Ref. No: . OC15000308 dated 18.01.2021
NEW COOLING TOWER CELL, COOLING WATER PUMP AND ASSOCIATED FACILITIES AT NUMALIGARH REFINERY LTD., ASSAM
S.No. | Reference |  | Description | Query | Response of NRL
| Section | Cl.no
1 | AGREED TERMS & CONDITIONS (ATC) | Sr. no. 5 | Defect Liability Period: The defect liability period shall be twelve (12) months from PGTR and acceptance of Cooling Tower & associated facility. | Please confirm that defect liability period shall be 12 months from commissioning or 18 months from mechanical completion, whichever is earlier. | Defect liability period is 12 months from date of issue of completion certificate.
2 | SCC | Cl. no.7 | PAYMENT TERMS & BILLING SCHEDULE: |  | Our payment terms is changed. Refer to the Annexure-I (corigendum).
3 | Technical Specification | Cl. no. 1.1 | Capacity = 2625 m3/hr/cell (Space available for the cell shall be surveyed by the party prior to submission of bid, capacity upto a minimum of 2500m3/hr/cell meeting all process related spec will be acceptable. | We understand that the minimum design capacity of the cooling tower is 2500m3/hr/cell. Please confirm. | Acceptable range for the design capacity is 2500 to 2625 M3/HR/CELL
4 | Technical Specification | Cl. no. 1.6 | All connecting Piping within Battery Limit……… | Please furnish the battery limit drawing duly indicating the terminal point locations. | The terminal points are within the battery limit (91m X 35m). The piping design including hookup also in the scope of the contract itself.
5 | Technical Specification | Cl. no. 3.1 | DESIGN DATA: Design Wet Bulb Temperature, (deg C): 27 The cooling tower to be designed for maximum wet bulb temperature of 29 deg C and Approach of 4 deg C. | Please specify the exact design WBT to be considered. | Design wet bulb temperature (Deg C) is 29 and design apprach is 4 deg C.
6 | Technical Specification | Cl. no. 4.5 | The material of construction of various items shall be as follows: Structural members: Confirming to CTI standard STD-137 latest edition Louvers: Confirming to CTI standard STD-137 latest edition | We understand that MOC of the structure will be Pultruded FRP. Please confirm. | MOC of structure is RCC. It is a RCC counter flow induced draft cooling tower conforming to IS:11504 1985, CTI ATC 105, CTI NCL 109, NFPA, NFC214 & NFC 780.
7 | Technical Specification | Cl. no. 4.5 | Pipe: IS 1239-1 Galvanised, Heavy schedule Pipe Flanges: SORF, A105, Galvanised, 150#, ANSI B 16.5 | The internal distribution header will be of FRP construction as per our tried and proven design. Please confirm. | Internal distribution header is FRP/ PVC
8 | Technical Specification | Cl. no. 4.5 | Spray nozzle: Nylon 6 | MOC of the nozzles will be polypropylene as per our tried and proven design. | MOC of nozzle Polypropylene/ Nylon 6
9 | Technical Specification | Cl. no. 4.14 | Air inlet louvers shall be suitably designed supported and arranged so that there will be minimum restriction to air flow and prevent down coming water from splashing out of tower. | Our counterflow design does not have louvers. | RCC counterflow induced draft cooling tower without air inlet louvers.
10 | Technical Specification | Cl. no. 4.18 | The basin shall have a holding capacity to retain 15 minutes of re-circulating water between minimum and normal water level. | As specified later in the same referred clause, the holding capacity of the basin shall be suitable for 10 minutes' flow. Besides, since the new cooling tower will be connected to the existing cooling tower, we understand that the basin levels of the new cell and the existing cells should be maintained at the same level. Please furnish the exact requirement. | Hold up capacity is 12 minutes
11 | Technical Specification | Cl. no. 4.18 | Successful bidder at his own cost shall get the design & drawings for basin vetted by third party i.e. by IITs/ NIT’s or by Certified & registered structural engineer ….. | Please furnish the list of documents / calculations to be vetted by third party i.e. by IITs/ NIT’s or by Certified & registered structural engineer. | Design, design calculations, construction drawings to be vetted by IIT/NIT's or certified registered structural engineer.
12 | Scope of Work / Supply (General Civil) | Cl. 1.1 | Details feasibility study, make-up water adequacy study and recommendations, system adequacy & fluid dynamic study | Please furnish the exact requirement and scope of feasibility study and adequacy check to be performed by the Contractor. | Study of existing system including coolig water system, make up water adequacy, system adequacy, fluid dynamic and make recommendations and design based on these studies are in the scope of the contractor.
13 | Soil Data Related Queries |  | Soil Data Related Queries | We require the following details for proposed Cooling Tower area 1) Existing Ground level and Finished Ground level 2) Soil investigation report along with the soil bearing capacity / Pile Capacity from Existing ground level/Finished ground level 3) Borelog data | All these are in the scope of design itself.
14 |  |  |  | Kindly furnish the following documents / information to enable us understand the scope and quantum of work. 1. Layout drawing with terminal point location 2. Interconnection scheme of Channel, Sump and pipes 3. Layout of the new cooling tower cell and associated facilities included in the tender | All these are in the scope of design itself.
15 |  |  |  | Kindly furnish the following technical datasheets & specifications. 1. Piping Material Specification 2. Valve Material Specification 3. Pumps specification 4. Mechanical datasheets of Cooling Tower and CW pump | The proposed additional cell is the replicate and extension of existing Process cooling tower. All these components should be design accordiingly.
16 | Cooling Tower | 1.3(IX) | Area all around the cooling tower basins and cold channel shall be provided with RCC Pavement Type-III as per Scope drawing. | Please provided width of RCC Pavement. | As per existing system and All these are in the scope of design itself.
17 | STRUCTURAL SCOPE OF WORK/ SUPPLY |  | (1) Please provide type of fill Ex. Film Type or Splash type. (2) No. of cells can be more than 2 or not as the space in not adequate for one cell of 13m X13m as per exiting Cooling Tower size. |  | The proposed additional cell is the replicate and extension of existing Process cooling tower. All these components should be design accordiingly.
18 | ROTATING EQUIPMENT SCOPE OF WORK/ SUPPLY |  | Cooling water centrifugal pump |  | The pump should be with mechanical seal. Recommended make Flowserve, EBIPL, Johncrane

## PAHARPUR 02
NEW COOLING TOWER CELL, COOLING WATER PUMP AND ASSOCIATED FACILITIES AT NUMALIGARH REFINERY LTD., ASSAM
ADDITIONAL PRE-BID CLARIFICATIONS
S.No. | Reference |  | Description | Query | Clarification
| Section | Cl.no
1 | P&ID DWG Number 25-02-41-A1-126 Rev 6/A | Note 5 | Hydrocarbon / Hydrogen & H2S detector for new cell to be provided at Cooling Tower top. Provision to be made by Cooling Tower Vendor. | We understand that for new cell pneumatic aspirator assembly type HC,H2S,H2 Gas detector to be considered in scope along with its Hooter/beacon unit and the Push button station unit for each type of HC,H2S,H2 Gas detector. Please confirm. | Yes. Hooter/Beacon with PB station to be installed in a manned area
2 | P&ID DWG Number 25-02-41-A1-126 Rev 6/A | Note 6 | Indication Lamp Vibration Switch and Alarm to be provided for Fan on Cooling Tower by Vendor. The motor should trip automatically on sensing vibration high limit, all indications to be provided on Local Panel in Cooling Tower block. | i. Please furnish technical specification & sub-vendor list of electronic type vibration switch. Please also indicate the number of vibration switches to be considered for each Fan motor. | i. We do not recommend Vibration Switch.
|  |  |  | ii. We alternatively propose to consider Loop powered Vibration transmitter NON HART Exia SIL type, in place of electronic type vibration switch. Please confirm. | ii. 4-20 loop 24 VDC loop powered non HART Exia SIL type Vibration Transmitter is acceptable
|  |  |  | iii. We understand tha the indication lamp mentioned in the spec. is for the Local Push Button station. Please confirm. | Confirmed . A running Indication contact from Electrical MCC to be provided for Remote Indication at Existing DCS
|  |  |  | iv. Please clarify whether the local panel referred in the spec. is the sub-package PLC ( for new facilities only ). | Yes
|  |  |  | v. Please clarify whether Bidder's scope includes wiring upto the PLC? | Bidder to provide Electrical Connection upto Existing DCS which includes Vibration Analog Signal (4-20 mA) , Running Indication , start/Stop and Trip signal of the Fan
3 | P&ID DWG Number 25-02-41-A1-126 Rev 6/A | Note 23 | UPS to be provided for control panel | Please clarify whether this clause is applicable for this new cell extension work. | As no new control Panel is there the query is not valid
4 | P&ID DWG Number 25-02-41-A1-126 Rev 6/A | Note 25 | Vibratiom Monitoring System (Bentley Nevada) shall be provided for new cell. | Please furnish detailed technical specification and number of vibration sensing points for the Gear Box / CT Fan motor. Please also clarify since Vibration monitoring system needs to be considered in scope whether vibration switches/transmitters for fan motor and gearbox need not be considered over and above the VMS. | VMS is not required. Accelerometers to be installed in the gear box DE & NDE side with long cables terminated in a junction box located outside the fan shroud. This gives the offline vibration taken in the scheduled route. Junction box should have BNC connector for acquiring data.
5 |  |  | Instruments for Gearbox | Please clarify whether the following instruments are to be considered by Bidder. 1. Gear Box Lube Oil level transmitter 2. Gear Box Lube Oil RTD and Temperature transmitter 3. Gear Box loop powered vibration transmitter | Yes, all these to be considered.
6 |  |  | Scope and Terminal points of wiring | Please furnish terminal point of wiring for the MOV of CW Pump discharge and fan deck instruments. | Wiring Diagram and Terminal details is to be provided by Vendor after finalization.. MOV should be with remote indication, remote/local operation, remote fault detection(high torque etc.) and the wiring diagram to provided by OEM/supplier. For fan deck instrument also wiring diagram to provide by vendor.
7 |  |  | Electrical & Instrumentation | Please furnish the detailed specification, scope of work, supply documents, terminal points list of electrical and instrumentation work. This is not clear from the tender documents. | All these are in the scope of the contract and it to be finalised at design engineering stage.
8 |  |  | Instruments for Sump Extension | We understand that no additional instruments are to be considered for sump extension. Please confirm. | Yes. No additiional instrument required.
9 |  |  |  | In case the Electrical and Instrumentation items needs to be suitable for hazardous area operation, kindly furnish the hazardous zone, gas group and temp. class to be considered for the same. | Zone-2 / IIC/T6
10 | P&ID DWG Number 25-02-41-A1-126 Rev 6/A |  | Time Delay Relay | a) Please confirm that the time delay relay circuit will be available in Purchaser's MCC end. b) Please furnish the details of interlock 'I' indicated in the P&ID. | No physical TDR is required in DCS end as it can be configured in Existing DCS (in soft). If TDR is required in MCC end EM will better comment. EM Comment: If time delay relay is w.r.t. to vibration trip , then there is no such delay presently in existing CT fans. It is as per vendor design.It can be incorporated in DCS (IM)
11 |  |  |  | Please clarify whether Corrosion monitoring rack / coupon to be considered by Bidder for new extension cell. | It is to consider
12 |  |  |  | We understand that HAZOP and SIL Study review is not applicable for this project. Please confirm. | As the project of additional cell in PCT is being done through MOC route, therefore internal HAZOP study has already has been done. SIL study is not required for the project.
13 |  |  |  | We have noted during discussions and site visit that piles for the 6th cell has been constructed during the earier phase of construction. Please confirm. | Piling not constructed in earlier phase of construction.
14 |  |  |  | We find that the sapce allocated for the new cell is narrow and inadequate to accommodate the cell. Kindly extend the area on the east side by atleast 2-3 M. | The cooling tower cell to design & contruct within the available space.
15 |  |  |  | Please clarify whether the existing staircase on the east face of the existing cooling tower to be dismantled. | Yes. Existing staircase to dismantled.
16 |  |  |  | Kindly share few site photographs of cooling tower extension area, CW sump, Channel, Header pipe and surrounding structures & facilities. | Some photographs are attached. Annexure III
17 |  |  |  | Please furnish the location of hooking up with the existing discharge header. | Location is not finalised. The same has to consider & finalised in the design engineering stage itself.
18 |  |  |  | Please furnish detail layout drawings of the cooling tower package area. | Drawings attached. Annexure IV

## PALTECK
Clause No. |  | NRL Specification | Paltech Query
|  | Given Two Design Wet Bulb Temperature |  | Design wet bulb temperature (Deg C) is 29 and design apprach is 4 deg C.
3.1 | Design Data | 27 (deg)C and 29 (deg)C | Please Clarify Whether we have to consider 27 (deg)C or 29 (deg) WBT for design
Given two Temperature Approach
|  | 6 (deg)C and 4 (deg)C | Please Clarify
| Material of Contruction | Given Structural members : CTI standard STD -137 | CTI standard-137 is applicable for Pultruded FRP cooling tower but MOC of cooling | MOC of structure is RCC. It is a RCC counter flow induced draft cooling tower conforming to IS:11504 1985, CTI ATC 105, CTI NCL 109, NFPA, NFC214 & NFC 780. Corigdum will be issued shortly.
4.5 | various items | latest edition | tower is RCC Please clarify moc for super structure.
Changed to without air inlet louvers. Corigdum will be issued shortly.
4.14 | Air inlet Louvers | The material of construction shall be preferably FRP | Air inlet Louvers Material of construction PVC please confirm.
4.25 | Drawings | Successful bidder at his | For only civil works shall be submitted kindly confirm | Design, design calculation, construction drawings to be vetted by IIT/NIT's or certified registered structural engineer.
own cost shall get the design & drawings vetted by third party i.e. by IITs/ NIT’s or by Certified & registered structural engineer and submit the same to NRL for approval and further clearances.
SCOPE OF WORKS / SUPPLY
(GENERAL CIVIL)
|  | Area all around the cooling tower basins and cold channel shall be provided with |  | Width of RCC pavement is 15250 MM
RCC Pavement Type-III as per Scope drawing.
1.3(IX) | Cooling Tower |  | Please provided width of RCC Pavement.
STRUCTURAL
SCOPE OF WORK/ SUPPLY
|  |  | (1) Please provide type of fill | All these are in the scope of design itself.
Ex. Film Type or Splash type
(2) No. of cells can be more than 2 or not as the space in not adequate for one cell of 13m X13m as per exiting Cooling Tower size.

## HAMON
SL.NO. | REFERENCE OF BIDDING DOCUMENT |  |  |  | BIDDER’S (HAMON COOLING SYSTEMS) QUERY DATED 28-01-021 | OWNER’S / PMC’s REPLY DATED
| PART / VOL. | PAGE NO. | CLAUSE NO. | SUBJECT
Technical Specification
1 | Unpriced Bid Documents | 2 of 44 |  | Contract Period : Complete jobs with all respect within 14 (Fourteen) months from date of issue of work order. | Considering the quantum of work involved in the integration major activities, we are proposing the completion period as eighteen (18) months from the date of techno-commercially clear LOA | No change
2 | Unpriced Bid Documents | 2 of 44 |  | SUBMISSION OF BIDS : Online EMD & Bid Submission: Before 11.00 AM of 17.02.2021 | Considering the quantum of work involved in preparation of bids as per the tender enquiry, site visit and pre-bid clarifications, we request NRL to extend the submission of bid up to 17.03.2021 | Bid due date extended upto 01.03.2021.
3 | Unpriced Bid Documents | 10 of 44 |  | DEFECT LIABILITY PERIOD: | We intend to consider the defect liability period as 12 months from the date of mechanical completion of cooling tower (as heat load & water load is dependent on readiness of other equipment and in the control of owner) or 18 months from the date of last major shipment, whichever is earlier. | Will be changed to : Defect liability period is 12 months from date of issue of completion certificate.
The defect liability period shall be twelve (12) months from PGTR and acceptance of Cooling Tower & associated facility
4 | Unpriced Bid Documents | 10 of 44 |  | RATE : Firm rate should be quoted | Considering the completion period and price fluctuations in raw materials, bought out items and labours etc., we request NRL to consider the price variation clause. | Price variation clause not applicable for this tender. Quoted rate should be firm.
5 | Unpriced Bid Documents | 4 of 44 |  | No mobilization advance will be paid to the contractor for execution of this work | We request NRL to consider interest free mobilization advance, as this will facilitate the smooth and speedy execution of the project. | No Mobilization advance applicable for this tender.
6 | General |  |  | Construction power supply | We request NRL to Clarify and provide the construction power as a free issue at a single point (10 mtr.) near cooling tower. | Single point construction water and electrical power shall be provided by NRL on free of charge basis subjected to availability. Contractor will have to make their own arrangement to tap power and water from the nearby source provided by NRL. Further, contractor may make their own arrangement for construction water & power in case of interruption in supply of these facilities by NRL. Any claim by contractor for delay in execution of the job due to disruption in water & power supply by NRL shall not be entertained.
7 | General |  |  | Construction water supply | We request NRL to Clarify and provide the construction power as a free issue at a single point (10 mtr.) near cooling tower.
8 | General |  |  | Land use for construction site offices and resident accommodation | We request NRL to provide the land for construction site offices, resident accommodation and land for temporary facilities | Only site office and stores are allowed.
9 | General |  |  | Land for temporary facilities | We request NRL to provide an area outside the plant at free of cost to build our labour camp. | Not applicable for NRL
Land for labour camp
10 | Technical Specification | 2 of 88 |  | Identical cooling tower cells | The new cooling tower cell dimensions and thermal calculations shall be as per our standard proprietary design. Please note. | Study, design, engineering are in the scope of the contract itself and it should be in line with our targeted specification.
11 | Technical Specification | 2 of 88 |  | SCOPE OF WORK : details feasibility study, make-up water adequacy study and recommendations, system adequacy & fluid dynamic study | The system feasibility study is a specialized nature of job and hence we request NRL to exclude from our scope of supply/work. Please note. | Technical feasibility study and generation of report is also in the scope of the contract
12 | Technical Specification | 3 of 88 |  | Vendor to guarantee the heat load, drifts loss at design capacity | The performance guarantee testing of drift loss involves significant price implication and hence we shall not conduct any testing for drift loss measurement and shall not guarantee the drift loss. | The test procedure ATC-105 of CTI (Acceptance Test Code for water Cooling Towers) to follow.
We shall indicate the drift loss value in the data sheet for reference. Kindly confirm.
13 | Technical Specification | 3 of 88 |  | Vendor to provide gas detection system (hydrocarbon & H2S) at new cooling tower top. | We request NRL to provide detail specification for the gas detection system | Pneumatic aspirator assembly type HC,H2S,H2 Gas detector to be considered in scope along with its Hooter/beacon unit and the Push button station unit for each type of HC,H2S,H2 Gas detector. Hooter/Beacon with PB station to be installed in a manned area
14 | Technical Specification | 5 of 88 | 4.5 | The material of construction | As per our standard design we provide the Polypropylene Nozzles. We request NRL to accept the same. | Acceptable material: Polypropylene/ Nylon 6.
Spray nozzle: Nylon 6
15 | Technical Specification | 5 of 88 | 4.8 | Civil jobs | We request NRL to provide the soil report taken at cooling tower area if available. | Not available
16 | Technical Specification | 6 of 88 | 4.17 | Vendor shall provide stairs for access to top deck | We request NRL to clarify shall we use the exiting staircase as common for Exiting cells and new cooling tower cells. Access will be done by hamon. | Alternative staircase to make. Existing staircase to dismantle.
17 | Scope of Works / Supply Cooling Tower | 12 of 88 | 1.3 | overflow arrangement which shall be suitably connected, to the nearest storm water drain | We request NRL to provide the distance to the nearest storm water drain | Within the battery limit
18 | Scope of Works / Supply Cooling Tower | 12 of 88 | 1.3. V | Corrosion probe and corrosion coupon | We request NRL to exclude from our scope of supply/work | It is needed.
19 | Scope of Works / Supply Cooling Tower | 14 of 88 | 1.6.I | Commissioning of the System | Our understanding is Flushing out of new installed pipes. NRL to Clarify | Yes, flushing out all new piping and equipments.
flushing out all piping
20 | CIVIL |  |  |  | We presume the following: | All these to be considered in the design engineering stage and all these are in the scope of the contract itself.
1) Soil investigation need not be carried out after award of contract.
2) NRL shall hand over the graded and levelled site before commencement of site works.
3) The approach roads if required shall be done by NRL.
4) The foundations for new cell cooling tower shall be same as existing tower. Kindly clarify
21 | General |  |  |  | Kindly provide the following: | Only for outside surface: ACRYLIC exterior emulsion paint --1 coat primer (50micron), 2 coat finished (50 micron each)
1) Painting specifications for inside surface and outside surface of cold-water basin, cold water channel, sump and super structure
22 | Commercial |  |  | Payment terms: | WE request NRL to reconsider the Payment Terms: | Payment terms are modified which will be incorporated in corrigendum.
|  |  |  | Design & Engineering: (3% Weightage) | For Supply
10% advance along with LOI / order.
|  |  |  | · 20% upon submission of reports, drawings and engineering details. | 10% Placement of orders
|  |  |  | · 20% upon Review/approval. | 70% against dispatch document on pro-rata basis
|  |  |  | · 20% on mechanical completion | 5% against mechanical completion
|  |  |  | · 20% on successful Commissioning of the PLANT. | 5% against Commissioning or 90 days from completion of erection, whichever is earlier.
|  |  |  | · 20% upon successful PERFORMANCE GUARANTEE TEST RUN and on completion of all jobs and issue of PROVISIONAL ACCEPTANCE CERTIFICATE. | All payments shall be released within 30 days of submission of invoice.
|  |  |  | Supplies : (40 % Weightage) | For Service
10% advance along with LOI / order.
|  |  |  | · 40% receipt of material as site along with test certificates, IRN & acceptance | 80% on pro-rata basis.
|  |  |  | · 20% upon mechanical completion | 5% against mechanical completion
|  |  |  | · 20% on successful Commissioning of the PLANT. | 5% against Commissioning or 90 days from completion of erection, whichever is earlier.
|  |  |  | · 20% upon successful PERFORMANCE GUARANTEE TEST RUN and on completion of all jobs and issue of PROVISIONAL ACCEPTANCE CERTIFICATE | All payments shall be released within 30 days of submission of invoice.
Construction, Erection & commissioning : (45 % Weightage)
· 80% upon execution of work, on pre-rata basis.
· 10% upon successful COMMISSIONING
· 10% upon successful PERFORMANCE GUARANTEE TEST RUN and on completion of all jobs and issue of PROVISIONAL ACCEPTANCE CERTIFICATE
Performance acceptance testing and submission of final documents (10 %)
On submission of final documentation including all as-built drawings,

## Additional Change
1 | SCOPE OF MATERIALS SUPPLY Scope of supply of all materials, tools & tackles, equipment and machineries and labour is entirely of contactor’s responsibility. However, in the interest of expediting the work NRL may supply cement, reinforcement bars, structural steels and other materials to the contractor on chargeable basis on their request and subject to availability at NRL. In such case the contractor has to lift the materials from NRL’s warehouse in Refinery premises and transport to the worksite at his own cost. NRL shall recover the landed cost of the materials (prevailing at the time of issuance) plus 15% overhead and applicable GST from contractor’s RA Bills or any other dues. However, any claim by contractor for delay in execution of the job due to non-issuance of material supply by NRL on Chargeable basis as mentioned above shall not be entertained.
2 | It will be Contractor's responsibility to bring to the notice of Engineer-in-Charge any irreconcilable conflict in various parts of Contract Documents before starting the works or making the supply with reference to which the conflict exists.
3 | In the absence of any specifications, for any material, design or works, the same shall be performed/ supplied/ executed in accordance with the instructions/ directions of the Engineerin- Charge, which will be binding on the Contractor.