## Tender no. OC15000290-CPP
Tender Reference No. : OC15000290 - Civil and Interior work of CPP New Control Room
Sl.no. | Query | From | Response
1.1 | The Fire alarm system specifications are very general and can be easily compiled by any standard entry level company. Besides as there is also no approved brand for the fire alarm system, on the basis of the price point , no major multinational brand like Bosch/Siemens/Edwards would prefer to quote as they would be outbidded. Please revert if it is acceptable for NRL Management to quote any standard brand as per technical specifications and it would not be an issue later on. The reason, i am asking this question is because the tender has been designed with the best brands and products in mind and it would be detrimental if fire alarm system would be of standard make. | Ashwini Saikia, Newtech Solutions | Recommended Makes of Intended Items of Fire Alarm & Detection System 1. Fire Alarm Panel - Honeywell / Edwards / Simplex/Agni/ Ravel/Equivalent 2. UL Listed GUI - Honeywell / Edwards / Simplex/ Agni/ Ravel / Equivalent 3. Detectors & Modules - Honeywell / Edwards / Simplex / Agni/ Ravel/ Equivalent 4. Isolator Module - Honeywell / Edwards / Simplex / Agni/ Ravel/ Equivalent 5. GUI Server - HP / Dell / Fujitsu / Lenovo/ Agni/ Ravel/ Equivalent 6. Signal & Power Cable - Polycab / Finolex / Havell’s / Technoflex / Neoflex/Equivalent 7. Fire Exit Signage - Prolite / Equivalent 8. Auto Dialer - Secure/ Agni/ Ravel /Equivalent
1.2 | As per the tender, all temporary structures like stores and office space are to be managed by erected and managed by the winning contractor. However, accommodation for employees deputed at project site as per hierarchy mentioned in the tender would be provided at NRL premises or would it have to be managed by the contractor outside of the NRL Campus/premises. | Ashwini Saikia, Newtech Solutions | No accommodation inside Refinery premises shall be allowed. Contractor has to arrange accommodation for their employees outside Refinery premises at their own cost

## Sheet1 (hidden)
QUERIES FOR TENDER no. - OC15000290 and TENDER no. - OC15000291
Sl.no. | Query | From | Response
1 | Recommended Makes of Intended Items of Fire Alarm & Detection System | Ashwini Saikia, Newtech Solutions | 1. Fire Alarm Panel - Honeywell / Edwards / Simplex/Agni/ Ravel/Equivalent (Recommended makes) 2. UL Listed GUI - Honeywell / Edwards / Simplex/ Agni/ Ravel / Equivalent (Recommended makes) 3. Detectors & Modules - Honeywell / Edwards / Simplex / Agni/ Ravel/ Equivalent (Recommended makes) 4. Isolator Module - Honeywell / Edwards / Simplex / Agni/ Ravel/ Equivalent (Recommended makes) 5. GUI Server - HP / Dell / Fujitsu / Lenovo/ Agni/ Ravel/ Equivalent (Recommended makes) 6. Signal & Power Cable - Polycab / Finolex / Havell’s / Technoflex / Neoflex/Equivalent (Recommended makes) 7. Fire Exit Signage - Prolite / Equivalent (Recommended makes) 8. Auto Dialer - Secure/ Agni/ Ravel /Equivalent (Recommended makes)
2.1 | Since due to the prevailing pandemic and lockdown, inter-district travel is disrupted. Can we have a video tour of the proposed site? | Sandeep Rajkhowa, AsthaCorp
2.2 | How much civil work is left in the proposed building?
2.3 | Are deviations in the certain recommended manufacturers allowed considering the nationwide lockdown and unavailability of certain materials on time.
2.4 | Can we apply in joint venture for the tender?
2.5 | We are well experienced in Mechanical, Electrical, Plumbing, HVAC, civil, furniture and fixture and interior fit-out works of educational institutions, large residential hostels and corporate offices. But in most of the cases, the agreements were for BOOT or BLT and are long term lease contracts and not outright handover to the client. Can that be considered for “Similar Works”?
2.6 | We are registered MSE and are below the threshold limit for EPF and ESI. However, if required, we shall register ourselves for both of the above. The certificates can be submitted in due course of time in the event of our selection for the work. Request you to kindly consider the same.
2.7 | We are registered MSE under MoMSME and may not meet the Annual Turnover criteria of Rs.138.28 Cr for all the previous three years. Can it be considered for applying for this tender?
2.8 | Are previous work orders / agreements be considered as valid prove for meeting the eligibility criteria?
2.9 | Request you to consider 4 projects of Rs. 70 Lakhs each in last three years in addition to the three mentioned qualification criteria of past experience.
2.1 | We are registered vendor under NRL and have worked earlier for the company. Will that be taken into consideration for short listing the above-mentioned tender?
2.11 | Are all the clauses under SPECIAL CONDITIONS FOR MICRO AND SMALL ENTERPRISES (MSEs) BIDDERS as per ANNEXURE X valid for this tender?
2.12 | Will there be any mobilization advance for the project?
3 | Incomplete List of Makes for the below-mentioned items : 1. Approved Make is not given for LTP Panel AC, Light Panel, Main LT Panel LT Panel STL. | Rohit Teotia, HLK INFRASTRUCTURE PVT. LTD. | Query 1. Any CPRI approved panel builder can be considered for all the panels.
| 2. Approved Make is not given for Switchgear of panel. | Rohit Teotia, HLK INFRASTRUCTURE PVT. LTD. | Query 2. Kindly refer to the list of recommended makes for switchgear which is similar for the panels too. However, a list especially for panels is enclosed herewith for better clarity where recommended makes for voltmeter, ammeter, indicating lamps, are also incorporated.
(1) LT PANEL- AC - INCOMER (refer SLD)- 1. FP MCCB of Rating 400A with Breaking Capacity 36KA with current limiting feature and electronic release with inbuilt E/F Protection, Ics=100%Icu extended rotary handle and spreader terminal - 1 No. (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 2. Digital Ammeter 0-500A 3 Phase 4 Wire Accuracy Class 1 as per IEC 62053-21 Bezel dimension (W X H)=96 X 96 mm: 1 No. (Recommended make - MECO /Automatic Electric Ltd/ Secure Meters Limited/ Rishabh Instruments Pvt Ltd. ) 3. Digital Voltmeter - 0-500V 3 Phase 4 Wire Accuracy Class 1 as per IEC 62053-21 Bezel dimension (W X H)=96 X 96 mm Communication capable by RS485/Modbus: 1 No. (Recommended make - MECO /Automatic Electric Ltd/ Secure Meters Limited/ Rishabh Instruments Pvt Ltd.) 4. CT 400/5 240V 3 Phase 4 wire Freq 50Hz+/- 5% Accuracy Class 0.5S-1 Set (Recommended make - L&T / Siemens / AEP / Kappa Electricals /AE) 5. SP MCB with 10KA breaking capacity of rating 6 Amp - 3 Nos (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 6. RYB Indicating Lamp - 1 Set (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 7. Bus-Bars: 800 A TPN electrolytic Aluminium Bus Bar of uniform cross-section – 1 set OUTGOING (refer SLD)- 1. FP MCCB of Rating 200A(Refer SLD) with Breaking Capacity 36KA with electronic release and inbuilt E/F Protection, Ics=100%Icu and spreader terminal - 1 No. (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 2. FP MCCB with 36KA Breaking Capacity of Rating 63A with E/F protection and Ics=100% Icu & adjustable overload setting of (0.8-1.0 × In) - 1 No. (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 3. FP MCB with 10KA Breaking capacity of Rating 63A and Qty 15 Nos. (Recommended make - L&T / Siemens / Legrand / Schneider/ABB)
(2) LIGHT PANEL - INCOMER (refer SLD)- 1. FP MCCB of Rating 100A with Breaking Capacity 25KA, extended rotary handle and spreader terminal - 1 No. with μP release (with 100 ms delay) and E/F (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 2. Digital Ammeter 0-500A 3 Phase 4 Wire Accuracy Class 1 as per IEC 62053-21 Bezel dimension (W X H)=96 X 96 mm: 1 No. (Recommended make - MECO /Automatic Electric Ltd/ Secure Meters Limited/ Rishabh Instruments Pvt Ltd) 3. Digital Voltmeter - 0-500V 3 Phase 4 Wire Accuracy Class 1 as per IEC 62053-21 Bezel dimension (W X H)=96 X 96 mm Communication capable by RS485/Modbus: 1 No. (Recommended make - MECO /Automatic Electric Ltd/ Secure Meters Limited/ Rishabh Instruments Pvt Ltd) 4. CT 100/5 240V 3 Phase 4 wire Freq 50Hz+/- 5% Accuracy Class 0.5S-1 Set (Recommended make - L&T / Siemens / AEP / Kappa Electricals /AE) 5. SP MCB with 10KA breaking capacity of rating 6 Amp - 3 Nos (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 6. RYB Indicating Lamp 1 Set (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 7. Bus-Bars: 200 A TPN electrolytic Aluminium Bus Bar of uniform cross-section – 1 set OUTGOING (refer SLD) - 1. DP MCB with 10 KA Breaking capacity of rating 25A amps – 9 nos (Recommended make - L&T / Siemens / Legrand / Schneider/ABB)
(3) MAIN LT PANEL- INCOMER (refer SLD) - 1. Automatic Transfer Switch of Rating 630A with Breaking Capacity 36KA, with UV/OV, phase sequence ,and single phasing protection and adjustible time delay - 1 no 2. FP MCCB of Rating 630A with Breaking Capacity 36KA, Ics=100 % Icu and adjustinle O/L protection(80-100%Icu) extended rotary handle and spreader terminal - 2 Nos. with electronic release and inbuilt E/F (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 3. Digital Ammeter 0-500A 3 Phase 4 Wire Accuracy Class 1 as per IEC 62053-21 Bezel dimension (W X H)=96 X 96 mm: 1 No. (Recommended make - MECO /Automatic Electric Ltd/ Secure Meters Limited/ Rishabh Instruments Pvt Ltd) 4. Digital Voltmeter - 0-500V 3 Phase 4 Wire Accuracy Class 1 as per IEC 62053-21 Bezel dimension (W X H)=96 X 96 mm Communication capable by RS485/Modbus: 1 No. (Recommended make - MECO /Automatic Electric Ltd/ Secure Meters Limited/ Rishabh Instruments Pvt Ltd) 5. CT 630/5 240V 3 Phase 4 wire Freq 50Hz+/- 5% Accuracy Class 0.5S-1 Set (Recommended make - L&T / Siemens / AEP / Kappa Electricals /AE) 6. CT 400/5 240V 3 Phase 4 wire Freq 50Hz+/- 5% Accuracy Class 0.5S-1 Set (Recommended make - L&T / Siemens / AEP / Kappa Electricals /AE) 7. CT 100/5 240V 3 Phase 4 wire Freq 50Hz+/- 5% Accuracy Class 0.5S-1 Set (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 8. SP MCB with 10KA breaking capacity of rating 6 Amp - 12 Nos (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 9. RYB Indicating Lamp - 4 Sets (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 10. Bus-Bars: 1250 A TPN electrolytic Aluminium Bus Bar of uniform cross-section – 1 set
OUTGOING (refer SLD) - 1. FP MCCB of Rating 400A with Breaking Capacity 36KA with current limiting feature and electronic release with inbuilt E/F Protection, Ics=100%Icu extended rotary handle and spreader terminal - 1 No. (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 2. Automatic Transfer Switch of Rating 125A with Breaking Capacity 36KA, with UV/OV, phase sequence ,and single phasing protection and adjustible time delay - 1 no (Recommended make - L&T / Siemens / Legrand / Schneider)
(4) LT PANEL - STL- INCOMER (refer SLD) - 1. FP MCCB of Rating 63A with Breaking Capacity 36KA, Ics=100%Icu, and adjustable O/L Relay range(80-100%Icu) extended rotary handle and spreader terminal - 1 No. with μP release and E/F (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 2. Astronomical timer switch with removable modules and 5 year battery warranty– 1 no. (Recommended make - L&T/ABB/Schneider) 3. Bus-Bars: 100 A TPN electrolytic Aluminium Bus Bar of uniform cross-section – 1 set OUTGOING (refer SLD) - 1. DP MCB with 10 KA Breaking capacity of rating 16A/10A/6A amps –16 nos (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 2. 16 amps switch and socket – 1 no. (Recommended make - L&T / Siemens / Legrand / Schneider/ABB) 3. 24" tube light with switch inside feeder pillar – 1 no. (Recommended make - Philips /Havells /Wipro /Trilux /Syska)
| 3. Some Light System’s Wattage is not given. | Rohit Teotia, HLK INFRASTRUCTURE PVT. LTD. | Query 3. The following are the wattage of luminaries to be considered (not given in the tender). (1) Recess-mounted Luminaire with white powder-coated CRCA housing with full window acrylic di user (2ft x 2ft) LED . [CLS] - 20 to 36 watts (2) Recess-mounted, COB-based, round xed LED downlight with 60 beam angle . [DLP] - 20 to 30 watts (3) LED surface-mounted, round panel with aluminium die cast housing luminaire . [DLS] - 6 to 12 watts (4) Recess-mounted, COB-based, round tiltable LED downlight with multiple beam angles (25°/ 36°) . [DLR] - 9 to 12 watts (5) Low depth, recess-mounted, sleek, round downlight with aluminium die cast housing & polycarbonate di user Downlights. [CLR] - 9 to 12 watts (6) LED BATTEN-TUBES with High quality aluminium extruded with decorative end caps. [TL] - 20 watts (7) Post top lantern [PTL] - 36 to 40 watts (8) Bollard light [BL] - 8 to 10 watts (9) LED Flood light [WL] - 50 watts (10) LED Bay light [VBL] - 70 watts
4 | SOR of Internal Electrical Works - (Item no. 960 - 990) Pl. Clarify whether including light fixture, If yes pl. mention details of light fixture. | Right Address | The item description itself speaks " including lamp, ballast as required. " Therefore it is inclusive of light fixtures.

## Sheet2 (hidden)
Annexure-II : RATING OF FEEDER PILLARS
Sl.No | Description
1 | LT PANEL- AC Supplying and installation of metal enclosed floor mounted front operated cubical type switch gear panel suitable for indoor installation conforming to IS: 8623 (Part I & II). Panel should be made of sheet steel and thickness not less than 2mm and structural steel having light section. The panel shall be completely dust tight and vermin proof(IP42) and shall be given seven tank anti-rust treatment as per IS and then powder coated (min 50 micron thick) in DA Grey colour. All wiring shall be PVC insulated and PVC sheathed of 1.1 KV grade of required size. The panel should have provision of entry of cable at the bottom and also provision of out going feeders from the bottom of the panel. Removable gland plates made with 2 mm thick sheet steel should be provided and the panel should be mounted on M.S angle iron frame made with 50mm X50mm X 5mm thick angle iron having 4 nos 450 mm long 50mm X50mm X 5mm thick angle iron legs. The bus bar shall be of high quality Aluminium of uniform cross sectionwithout fissures. The panel shall consist of the following items (viz.Digital Voltmeter(0-500V), Ammeter(0-500A), CT(400/5), indicating lamps, etc.) connected as per drawing and shall be flush mounted on the front of the panel. Contractor should submit the GA Drawing of panel board and obtain necessary approval for authority before placing purchase P.O. of the panel board.
INCOMER (refer SLD)
| 1. FP MCCB of Rating 400A with Breaking Capacity 36KA with current limiting feature and electronic release with inbuilt E/F Protection, Ics=100%Icu extended rotary handle and spreader terminal - 1 No. | 1. 400A, 4P, MCCB, 36 KA - 1 No with μP release and E/F | L&T / Siemens / Legrand / Schneider/ABB
| 2. Digital Ammeter 0-500A 3 Phase 4 Wire Accuracy Class 1 as per IEC 62053-21 Bezel dimension (W X H)=96 X 96 mm: 1 No. | 2. Digital Ammeter - 1 No. | MECO /Automatic Electric Ltd/ Secure Meters Limited/ Rishabh Instruments Pvt Ltd
| 3. Digital Voltmeter - 0-500V 3 Phase 4 Wire Accuracy Class 1 as per IEC 62053-21 Bezel dimension (W X H)=96 X 96 mm Communication capable by RS485/Modbus: 1 No. | 3. Digital Voltmeter - 1 No. | MECO /Automatic Electric Ltd/ Secure Meters Limited/ Rishabh Instruments Pvt Ltd
| 4. CT 400/5 240V 3 Phase 4 wire Freq 50Hz+/- 5% Accuracy Class 0.5S-1 Set | 4. CT 400/5 -1 Set | L&T / Siemens / AEP / Kappa Electricals /AE
| 5. SP MCB with 10KA breaking capacity of rating 6 Amp - 3 Nos | 5. Switch Fuse Unit - 3 Nos | L&T / Siemens / Legrand / Schneider/ABB
| 6. RYB Indicating Lamp 1 Set | 7. RYB Indicating Lamp 1 Set | L&T / Siemens / Legrand / Schneider/ABB
| 7. Bus-Bars: 800 A TPN electrolytic Aluminium Bus Bar of uniform cross-section – 1 set | 8. Bus-Bars: 800 A TPN electrolytic Aluminium Bus Bar of uniform cross-section – 1 set
OUTGOING (refer SLD)
| 1. FP MCCB of Rating 200A(Refer SLD) with Breaking Capacity 36KA with electronic release and inbuilt E/F Protection, Ics=100%Icu and spreader terminal - 1 No. | 1. 200A, 4P, MCCB, 36 KA - 1 No. | L&T / Siemens / Legrand / Schneider/ABB
| 2. FP MCCB with 36KA Breaking Capacity of Rating 63A with E/F protection and Ics=100% Icu & adjustable overload setting of (0.8-1.0 × In) - 1No. | 2. 63A, 4P, MCCB, 36 KA - 1 No. | L&T / Siemens / Legrand / Schneider/ABB
| 3. FP MCB with 10KA Breaking capacity of Rating 63A and Qty 15 Nos. | 3. 63A, 4P, MCB, 10 KA - 9 Nos. | L&T / Siemens / Legrand / Schneider/ABB
2
LIGHT PANEL Supplying and installation of metal enclosed floor mounted front operated cubical type switch gear panel suitable for indoor installation conforming to IS: 8623 (Part I & II). Panel should be made of sheet steel and thickness not less than 2mm and structural steel having light section. The panel shall be completely dust tight and vermin proof and shall be given seven tank anti-rust treatment as per IS and then powder coated (min 50 micron thick) in DA Grey colour.All wiring shall be PVC insulated and PVC sheathed of 1100 volt grade of required size. The panel should have provision of entry of cable at the bottom and also provision of out going feeders from the bottom of the panel. Removable gland plates made with 2 mm thick sheet steel should be provided and the panel should be mounted on M.S angle iron frame made with 50mm X50mm X 5mm thick angle iron having 4 nos 450 mm long 50mm X50mm X 5mm thick angle iron legs. Removable gland plates made with 2 mm thick sheet steel should be provided and the panel should be mounted on M.S angle iron frame made with 50mm X50mm X 5mm thick angle iron having 4 nos 450 mm long 50mm X50mm X 5mm thick angle iron legs. The bus bar shall be of high quality Aluminium of uniform cross section. The bus bar shall be of high quality Aluminium of uniform cross section without fissures. The panel shall consist of the following items (viz.Digital Voltmeter(0-500V), Ammeter(0-100A), CT(100/5), indicating lamps, etc.) connected as per drawing and shall be flush mounted on the front of the panel. Contractor should submit the GA Drawing of panel board and obtain necessary approval for authority before placing purchase P.O. of the panel board.
INCOMER (refer SLD)
| 1. FP MCCB of Rating 100A with Breaking Capacity 25KA, extended rotary handle and spreader terminal - 1 No. with μP release (with 100 ms delay) and E/F | 1. 100A, 4P, MCCB, 25 KA - 1 No. with μP release and E/F | L&T / Siemens / Legrand / Schneider/ABB
| 2. Digital Ammeter 0-500A 3 Phase 4 Wire Accuracy Class 1 as per IEC 62053-21 Bezel dimension (W X H)=96 X 96 mm: 1 No. | 2. Digital Ammeter - 1 No. | MECO /Automatic Electric Ltd/ Secure Meters Limited/ Rishabh Instruments Pvt Ltd
| 3. Digital Voltmeter - 0-500V 3 Phase 4 Wire Accuracy Class 1 as per IEC 62053-21 Bezel dimension (W X H)=96 X 96 mm Communication capable by RS485/Modbus: 1 No. | 3. Digital Voltmeter - 1 No. | MECO /Automatic Electric Ltd/ Secure Meters Limited/ Rishabh Instruments Pvt Ltd
| 4. CT 100/5 240V 3 Phase 4 wire Freq 50Hz+/- 5% Accuracy Class 0.5S-1 Set | 4. CT 100/5 -1 Set | L&T / Siemens / AEP / Kappa Electricals /AE
| 5. SP MCB with 10KA breaking capacity of rating 6 Amp - 3 Nos | 5. Switch Fuse Unit - 3 Nos | L&T / Siemens / Legrand / Schneider/ABB
| 6. RYB Indicating Lamp 1 Set | 7. RYB Indicating Lamp 1 Set | L&T / Siemens / Legrand / Schneider/ABB
| 7. Bus-Bars: 200 A TPN electrolytic Aluminium Bus Bar of uniform cross-section – 1 set | 8. Bus-Bars: 200 A TPN electrolytic Aluminium Bus Bar of uniform cross-section – 1 set
OUTGOING (refer SLD)
| 1. DP MCB with 10 KA Breaking capacity of rating 25A amps – 9 nos | 1. 25A, DP, MCB, 10 KA - 9 Nos. | L&T / Siemens / Legrand / Schneider/ABB
3
MAIN LT PANEL Supplying and installation of metal enclosed floor mounted front operated cubical type switch gear panel suitable for indoor installation conforming to IS: 8623 (Part I & II). Panel should be made of sheet steel and thickness not less than 2mm and structural steel having light section. The panel shall be completely dust tight and vermin proof and shall be given seven tank anti-rust treatment as per IS and then powder coated (min 50 micron thick) in DA Grey colour. All wiring shall be PVC insulated and PVC sheathed of 1.1KV grade of required size. The panel should have provision of entry of cable at the bottom and also provision of out going feeders from the bottom of the panel. Removable gland plates made with 2 mm thick sheet steel should be provided and the panel should be mounted on M.S angle iron frame made with 50mm X50mm X 5mm thick angle iron having 4 nos 450 mm long 50mm X50mm X 5mm thick angle iron legs. The bus bar shall be of high quality Aluminium of uniform cross section. The panel shall consist of the following items (viz.Digital Voltmeter(0-500V), Ammeter(0-800A), CTs, indicating lamps, etc.) connected as per drawing and shall be flush mounted on the front of the panel. Contractor should submit the GA Drawing of panel board and obtain necessary approval for authority before placing purchase P.O. of the panel board.
INCOMER (refer SLD)
| 1. Automatic Transfer Switch of Rating 630A with Breaking Capacity 36KA, with UV/OV, phase sequence ,and single phasing protection and adjustible time delay - 1 no | 1. Automatic Transfer Switch with 2 nos. 630A, 4P, MCCB, 36 KA - 1 Set with μP release and E/F
| 2. FP MCCB of Rating 630A with Breaking Capacity 36KA, Ics=100 % Icu and adjustinle O/L protection(80-100%Icu) extended rotary handle and spreader terminal - 2 Nos. with electronic release and inbuilt E/F | 2. 100A, 4P, MCCB, 36 KA - 1 No. with μP release and E/F | L&T / Siemens / Legrand / Schneider/ABB
| 3. Digital Ammeter 0-500A 3 Phase 4 Wire Accuracy Class 1 as per IEC 62053-21 Bezel dimension (W X H)=96 X 96 mm: 1 No. | 3. Digital Ammeter - 4 Nos. | MECO /Automatic Electric Ltd/ Secure Meters Limited/ Rishabh Instruments Pvt Ltd
| 4. Digital Voltmeter - 0-500V 3 Phase 4 Wire Accuracy Class 1 as per IEC 62053-21 Bezel dimension (W X H)=96 X 96 mm Communication capable by RS485/Modbus: 1 No. | 4. Digital Voltmeter - 4 Nos. | MECO /Automatic Electric Ltd/ Secure Meters Limited/ Rishabh Instruments Pvt Ltd
| 5. CT 630/5 240V 3 Phase 4 wire Freq 50Hz+/- 5% Accuracy Class 0.5S-1 Set | 5. CT 630/5 -1 Set | L&T / Siemens / AEP / Kappa Electricals /AE
| 6. CT 400/5 240V 3 Phase 4 wire Freq 50Hz+/- 5% Accuracy Class 0.5S-1 Set | 6. CT 400/5 -1 Set | L&T / Siemens / AEP / Kappa Electricals /AE
| 7. CT 100/5 240V 3 Phase 4 wire Freq 50Hz+/- 5% Accuracy Class 0.5S-1 Set | 7. CT 100/5 -2 Sets | L&T / Siemens / Legrand / Schneider/ABB
| 8. SP MCB with 10KA breaking capacity of rating 6 Amp - 12 Nos | 8. Switch Fuse Unit - 12 Nos | L&T / Siemens / Legrand / Schneider/ABB
| 9. RYB Indicating Lamp 4 Sets | 10. RYB Indicating Lamp 4 Sets | L&T / Siemens / Legrand / Schneider/ABB
| 10. Bus-Bars: 1250 A TPN electrolytic Aluminium Bus Bar of uniform cross-section – 1 set | 11. Bus-Bars: 1250 A TPN electrolytic Aluminium Bus Bar of uniform cross-section – 1 set
OUTGOING (refer SLD)
| 1. FP MCCB of Rating 400A with Breaking Capacity 36KA with current limiting feature and electronic release with inbuilt E/F Protection, Ics=100%Icu extended rotary handle and spreader terminal - 1 No. | 1. 400A, 4P, MCCB, 36 KA - 1 No. | L&T / Siemens / Legrand / Schneider/ABB
| 2. Automatic Transfer Switch of Rating 125A with Breaking Capacity 36KA, with UV/OV, phase sequence ,and single phasing protection and adjustible time delay - 1 no | 2. Automatic Transfer Switch with 2 nos. 100A, 4P, MCCB, 36 KA - 1 Set | L&T / Siemens / Legrand / Schneider
4
LT PANEL - STL
Supplying and installation of metal enclosed floor mounted front operated cubical type switch gear panel suitable for indoor installation conforming to IS: 8623 (Part I & II). Panel should be made of sheet steel and thickness not less than 2mm and structural steel having light section. The panel shall be completely dust tight and vermin proof (IP54) and shall be given seven tank anti-rust treatment as per IS and then powder coated (min 50 micron thick) in DA Grey colour.All wiring shall be PVC insulated and PVC sheathed of 1.1KV grade of required size. The panel should have provision of entry of cable at the bottom and also provision of out going feeders from the bottom of the panel. Removable gland plates made with 2 mm thick sheet steel should be provided and the panel should be mounted on M.S angle iron frame made with 50mm X50mm X 5mm thick angle iron having 4 nos 450 mm long 50mm X50mm X 5mm thick angle iron legs.The bus bar shall be of high quality Aluminium of uniform cross section. The panel shall consist of the following items (viz.Digital Voltmeter(0-500V), Ammeter(0-100A), CT(100/5), indicating lamps, etc.) connected as per drawing and shall be flush mounted on the front of the panel. Canopy type sloping roof, in addition to the main enclosure roof, shall be provided to prevent accumulation of rain water and provide additional protection against water leakage. The roof extension shall cover the top side of doors to prevent leakage of water. Overhang portion shall be minimum 300mm on each side. Contractor should submit the GA Drawing of panel board and obtain necessary approval for authority before placing purchase P.O. of the panel board.
INCOMER (refer SLD)
| 1. FP MCCB of Rating 63A with Breaking Capacity 36KA, Ics=100%Icu, and adjustable O/L Relay range(80-100%Icu) extended rotary handle and spreader terminal - 1 No. with μP release and E/F | 1. 63A, 4P, MCCB, 36 KA - 1 No. with μP release and E/F | L&T / Siemens / Legrand / Schneider/ABB
| 2. Astronomical timer switch with removable modules and 5 year battery warranty– 1 no. | 2. Astronomical timer switch – 1 no. | L&T/ABB/Schneider
| 3. Bus-Bars: 100 A TPN electrolytic Aluminium Bus Bar of uniform cross-section – 1 set | 3. Bus-Bars: 100 A TPN electrolytic Aluminium Bus Bar of uniform cross-section – 1 set
OUTGOING (refer SLD)
| 1. DP MCB with 10 KA Breaking capacity of rating 16A/10A/6A amps –16 nos | 1. 16A/10A/6A, DP, MCB, 10 KA - 16 Nos. | L&T / Siemens / Legrand / Schneider/ABB
| 2. 16 amps switch and socket – 1 no. | 2. 16 amps switch and socket – 1 no. | L&T / Siemens / Legrand / Schneider/ABB
| 3. 24" tube light with switch inside feeder pillar – 1 no. | 3. 24" tube light with switch inside feeder pillar – 1 no. | Philips/Havells/Wipro/Trilux/Syska

## Sheet3 (hidden)
| Luminaries | Wattage
1 | Recess-mounted Luminaire with white powder-coated CRCA housing with full window acrylic di user (2ft x 2ft) LED . [CLS] | 20 to 36 watts
2 | Recess-mounted, COB-based, round xed LED downlight with 60 beam angle . [DLP] | 20 to 30 watts
3 | LED surface-mounted, round panel with aluminium die cast housing luminaire . [DLS] | 6 to 12 watts
4 | Recess-mounted, COB-based, round tiltable LED downlight with multiple beam angles (25°/ 36°) . [DLR] | 9 to 12 watts
5 | Low depth, recess-mounted, sleek, round downlight with aluminium die cast housing & polycarbonate di user Downlights. [CLR] | 9 to 12 watts
6 | LED BATTEN-TUBES with High quality aluminium extruded with decorative end caps. [TL] | 20 watts
7 | Post top lantern [PTL] | 36 to 40 watts
8 | Bollard light [BL] | 8 to 10 watts
9 | LED Flood light [WL] | 50 watts
10 | LED Bay light [VBL] | 70 watts