## ENV TABLE I
QUARTERLY PERFORMANCE REPORT W.R.T ENIVRONMENTAL ASPECT
TABLE-I 'TREATED EFFLUENT MONITORING DATA -DURING QR. IV (JAN-MARCH, 21) 2020-2021
MONITORED VALUES in mg/lit.except pH
SL. NO | PARAMETERS | NO. OF OBS | MAX. | MIN. | AVG. | Limiting value for conc. (mg/l except for pH) | Quantum limit in Kg / 1000 MT of crude processed
[7 empty] | Actual | Standard
1 | pH | 91 | 7.5 | 7 | 7.4367 | 6-8.5 | - | -
2 | OIL & GRE | 91 | 4.9 | 2.8 | 4.05 | 5 | 1.8 | 2
3 | SULPHIDE | 91 | <0.1 | <0.1 | <0.1 | 0.5 | 0.04 | 0.2
4 | PHENOL | 91 | 0.35 | 0.08 | 0.24 | 0.35 | 0.11 | 0.14
5 | S. SOLID | 91 | 18 | 10 | 13.9 | 20 | 6.19 | 8
6 | COD | 91 | 122 | 37 | 71.7 | 125 | 3.19 | 50
7 | BOD3 | 91 | 15 | 10 | 5.1633 | 15 | 1.2 | 6
8 | CN | 91 | <0.02 | <0.02 | <0.02 | 0.2 | 0.01 | 0.08
9 | Ammonia as N | 3 | 12 |  | 10.2667 | 15 | 4.57 | 6
10 | Cr (Hexavalent) | 3 | 0 |  | 0 | 0.1 | 0 | 0.04
11 | Cr (Total) | 3 | 0.03 |  | 0.019667 | 2 | 0.009 | 0.8
12 | Pb | 3 | 0.32 |  | 0.017333 | 0.1 | 0.008 | 0.04
13 | Zn | 3 | 0.01 |  | 0.01 | 5 | 0.004 | 2
14 | Ni | 3 | 0.05 |  | 0.021333 | 1 | 0.009 | 0.4
15 | Cu | 3 | 0.08 |  | 0.033333 | 1 | 0.01 | 0.4
16 | Benzene | 3 | 0.063 |  | 0.054667 | 0.1 | 0.024 | 0.04
17 | Benzo (a)- Pyrene | 3 | 0.069 |  | 0.054 | 0.2 | 0.024 | 0.08
18 | Hg | 3 | 0.006 |  | 0.0046667 | 0.01 | 0 | 0.004
19 | V | 3 | 0.091 |  | 0.085 | 0.2 | 0 | 0.8
20 | TKN | 3 | 23.4 |  | 19.4333 | 40 | 8.65 | 16
21 | P | 3 | 1.22 |  | 0.8 | 3 | 0.44 | 1.2
Limiting concentration of effluent is as per MoEF notification on standard vide GSR-186 (E)dated 18th March, 2008.
* BDL- Detectable Limit : 0.1 microgram/Litre
* Parameters from 9 to 21 are monitored once in a month as per CPCB norms

## ENV TABLE II
QUARTERLY PERFORMANCE REPORT W.R.T ENVIRONMENTAL ASPECT.
TABLE-II 'STACK MONITORING DATA ': DURING QUARTER IV (JAN-MARCH,21),2020-21
Online Stack Analyser data
UNIT | FURNACE STACK | PARAMETER | OBSERVED VALUE |  | Limiting Concentration in mg/Nm3 | Remarks Limit conc. calculated using fuel type& quan. used during the period
CONC. (In mg/Nm3)
|  |  | MAX. | MIN.
CDU/VDU | FF-01/02 | SO2 | 525.36 | 8.67 | 569 | Stack with dual firing (FG:FO=69:31)
|  | NOX | 100.53 | 28.1 | 381
|  | CO | 8.38 | 4.25 | 166
DCU | FF-01 | SO2 | 282.74 | 7.71 | 891 | Stack with dual firing (FG:FO=49:51)
|  | NOX | 327.12 | 9.23 | 401
HCU | FF-01/02 | SO2 | 33.7 | 1.82 | 50 | Stack with Gas firing
|  | NOX | 34.7 | 5.56 | 350
HCU | FF-03 | SO2 | 126 | 9.42 | 190 | Stack with dual firing (FG:FO=92:8)
|  | NOX | 139.55 | 3.49 | 358
H2U | FF-01 | SO2 | 47.24 | 5.55 | 50 | Stack with Gas firing
|  | NOX | 57.21 | 1.72 | 350
MSP | FF-01 | SO2 | 35.7 | 13.2 | 50 | Stack with Gas firing
|  | NOX | 88.48 | 14.29 | 350
CPP HRSG |  | SO2 | 21.54 | 8.48 | 50 | Stack with dual firing (FG:NAP=100:00)
|  | NOX | 23.2 | 4.6 | 350
CPP UTILITY BOILER |  | SO2 | 41.69 | 17.77 | 50 | Stack with Dual firing (FG:FO=100:0)
|  | NOX | 107.05 | 5.58 | 350
DHDT |  | SO2 | 28.5 | 3.13 | 50 | Stack with Gas firing
|  | NOX | 97.75 | 4.9 | 350
* Limiting concentration of emission calculated as per MOEF new notification on standard vide GSR- 186 (E) dated 18th March, 2008. Emission level for all the stacks are found to be within limit

## ENV TABLE III
NUMALIGARH REFINERY LIMITED
QUARTERLY PERFORMANCE WITH RESPECT TO ENVIRONMENTAL ASPECTS
TABLE -III 'AAQ MONITORING DATA ' : DURING QUARTER IV(JAN-MARCH,21), 2020-21
Ambient Air Quality Data
STATION | PARAMETER | STD | Unit | OBSERVATIONS
|  | NAAQS-2009 |  | MAX | MIN | AVG
REFINERY (WATCH TOWER NO. 6) | SO2 | 80 (24 hr avg.) | μg/m3 | 13.9 | 9.2 | 11.75
| NO2 | 80 (24 hr avg.) | μg/m3 | 17.7 | 12.6 | 15.4433
| O3 | 100 (8 hr avg.) | μg/m3 | 38.3 | 16.2 | 25.2067
| CO | 2.000 (8 hr.avg.) | mg/m3 | 1 | 0.69 | 0.87
| NH3 | 400 (24 hr.avg.) | μg/m3 | 32.4 | 16.3 | 24.55
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 64.8 | 47.2 | 55.4633
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 35.6 | 20 | 25.3933
| Benzene | 05 (Annual) | μg/m3 | 3.3 | 1.3 | 2.22
| HC |  | mg/m3 | 1.21 | 0.72 | 1
| BaP | 01 (Annual) | ng/m3 | 0.5 | 0.5 | 0.5
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.44 | 0.17 | 0.28667
| As | 06 (Annual) | ng/m3 | 1 | 1 | 1
| Ni | 20 (Annual) | ng/m3 | 3.9 | 1.6 | 2.77
ECO-PARK IN NRL TOWNSHIP | SO2 | 80 (24 hr avg.) | μg/m3 | 13.6 | 8.8 | 10.9367
| NO2 | 80 (24 hr avg.) | μg/m3 | 19 | 11.7 | 14.6133
| O3 | 100 (8 hr avg.) | μg/m3 | 34.5 | 17.1 | 26.9
| CO | 2.000 (8 hr.avg.) | mg/m3 | 0.92 | 0.69 | 0.79333
| NH3 | 400 (24 hr.avg.) | μg/m3 | 30.9 | 16.3 | 23.81
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 57.8 | 44.9 | 51.94
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 29.9 | 16.1 | 23.0967
| Benzene | 05 (Annual) | μg/m3 | 3.2 | 1.2 | 2.1367
| HC |  | mg/m3 | 1.16 | 0.69 | 0.95
| BaP | 1.0 (Annual) | ng/m3 | 0.5 | 0.5 | 0.5
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.41 | 0.17 | 0.27333
| As | 6.0 (Annual) | ng/m3 | 1 | 1 | 1
| Ni | 20 (Annual) | ng/m3 | 3.8 | 1.4 | 2.3433
RAW WATER INTAKE | SO2 | 80 (24 hr avg.) | μg/m3 | 12.3 | 8.5 | 10.4467
| NO2 | 80 (24 hr avg.) | μg/m3 | 16.7 | 10.9 | 13.96
| O3 | 100 (8 hr avg.) | μg/m3 | 32.3 | 14.3 | 23.9633
| CO | 2.000 (8 hr.avg.) | mg/m3 | 0.9 | 0.61 | 0.75667
| NH3 | 400 (24 hr.avg.) | μg/m3 | 30 | 14.8 | 22.76
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 58.2 | 42 | 49.4433
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 30.8 | 16.9 | 22.7067
| Benzene | 05 (Annual) | μg/m3 | 2.8 | 1.1 | 2.0433
| HC |  | mg/m3 | 1.07 | 0.61 | 0.83333
| BaP | 01 (Annual) | ng/m3 | 0.5 | 0.5 | 0.5
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.37 | 0.15 | 0.26333
| As | 06 (Annual) | ng/m3 | 1 | 1 | 1
| Ni | 20 (Annual) | ng/m3 | 3.7 | 1.2 | 2.4833
NH-39 BYPASS | SO2 | 80 (24 hr avg.) | μg/m3 | 15.9 | 10.6 | 12.8233
| NO2 | 80 (24 hr avg.) | μg/m3 | 21.3 | 13.5 | 16.9
| O3 | 100 (8 hr avg.) | μg/m3 | 41.6 | 19.7 | 31.0567
| CO | 2.000 (8 hr.avg.) | mg/m3 | 1.19 | 0.82 | 10.6633
| NH3 | 400 (24 hr.avg.) | μg/m3 | 39.1 | 20.2 | 30.11
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 74.9 | 55.3 | 63.3333
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 38.2 | 19.5 | 26.81
| Benzene | 05 (Annual) | μg/m3 | 4.1 | 1.4 | 2.59
| HC | - | mg/m3 | 1.39 | 0.79 | 1.1
| BaP | 1 | ng/m3 | 0.5 | 0.5 | 0.5
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.47 | 0.21 | 0.34333
| As | 6 | ng/m3 | 1 | 1 | 1
| Ni | 20 (Annual) | ng/m3 | 4.7 | 1.6 | 2.9167
KAZIRANGA WILDLIFE SANCTUARY AT AGARTOLI | SO2 | 80 (24 hr avg.) | μg/m3 | 11.5 | 7.9 | 9.6167
| NO2 | 80 (24 hr avg.) | μg/m3 | 15.1 | 10.2 | 12.54
| O3 | 100 (8 hr avg.) | μg/m3 | 30.5 | 14.1 | 23.8667
| CO | 2.000 (8 hr.avg.) | mg/m3 | 0.87 | 0.59 | 0.70667
| NH3 | 400 (24 hr.avg.) | μg/m3 | 29.1 | 13.6 | 19.5567
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 53.1 | 41.7 | 46.6033
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 24.7 | 16.5 | 20.2267
| Benzene | 05 (Annual) | μg/m3 | 3 | 1.2 | 8.0067
| HC | - | mg/m3 | 1.01 | 0.59 | 0.83333
| BaP | 1 | ng/m3 | 0.5 | 0.5 | 0.5
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.36 | 0.15 | 0.27
| As | 6 | ng/m3 | 1 | 1 | 1
| Ni | 20 (Annual) | ng/m3 | 3.4 | 1.6 | 2.35
BDL:Below Detection Level, All the parameters are found to be within limt