## ENV TABLE II
QUARTERLY PERFORMANCE REPORT W.R.T ENIVRONMENTAL ASPECT
DURING QR. I (APRIL -JUNE , 21) 2021 -22
TABLE-1 LIQUID EFFLUENT POLLUTANT LEVEL -
MONITORED VALUES in mg/lit.except pH
SL. NO | PARAMETERS | NO. OF OBS | MAX. | MIN. | AVG. | Limiting value for conc. (mg/l except for pH) | Quantum limit in Kg / 1000 MT of crude processed
[7 empty] | Actual | Standard
1 | pH | 91 | 7.8 | 7 | 7.3767 | 6-8.5 | - | -
2 | OIL & GRE | 91 | 5 | 1.9 | 3.4833 | 5 | 1.8 | 2
3 | SULPHIDE | 91 | <0.1 | <0.1 | <0.1 | 0.5 | 0.05 | 0.2
4 | PHENOL | 91 | 0.34 | 0.1 | 0.20333 | 0.35 | 0.31 | 0.14
5 | S. SOLID | 91 | 20 | 10 | 15.1333 | 20 | 7.8 | 8
6 | COD | 91 | 123 | 43 | 73.8 | 125 | 38.1 | 50
7 | BOD3 | 91 | 15 | 8 | 10.3333 | 15 | 5.33 | 6
8 | CN | 91 | <0.02 | <0.02 | <0.02 | 0.2 | 0.01 | 0.08
9 | Ammonia as N | 3 | 13 |  | 10.5667 | 15 | 5.45 | 6
10 | Cr (Hexavalent) | 3 | 0 |  | 0 | 0.1 | 0 | 0.04
11 | Cr (Total) | 3 | 0.01 |  | 0.011667 | 2 | 0.01 | 0.8
12 | Pb | 3 | 0.02 |  | 0.011667 | 0.1 | 0.006 | 0.04
13 | Zn | 3 | 0.07 |  | 0.076667 | 5 | 0.04 | 2
14 | Ni | 3 | 0.05 |  | 0.02 | 1 | 0.01 | 0.4
15 | Cu | 3 | 0.06 |  | 0.027 | 1 | 0.014 | 0.4
16 | Benzene | 3 | 0.07 |  | 0.053667 | 0.1 | 0.028 | 0.04
17 | Benzo (a)- Pyrene | 3 | 0.083 |  | 0.062667 | 0.2 | 0.032 | 0.08
18 | Hg | 3 | 0.005 |  | 0.0043333 | 0.01 | 0 | 0.004
19 | V | 3 | 0.098 |  | 0.081333 | 0.2 | 0 | 0.8
20 | TKN | 3 | 21.4 |  | 18.8667 | 40 | 9.73 | 16
21 | P | 3 | 1.3 |  | 1.2133 | 3 | 0.63 | 1.2
Limiting concentration of effluent is as per MoEF notification on standard vide GSR-186 (E)dated 18th March, 2008.
* BDL- Detectable Limit : 0.1 microgram/Litre
* Parameters from 9 to 21 are monitored once in a month as per CPCB norms

## ENV TABLE III
QUARTERLY PERFORMANCE REPORT W.R.T ENVIRONMENTAL ASPECT.
DURING QUARTER I(APRIL-JUNE,21),2021-22
Online Stack Analyser data
UNIT | FURNACE STACK | PARAMETER | OBSERVED VALUE |  | Limiting Concentration in mg/Nm3 | Remarks Limit conc. calculated using fuel type& quan. used during the period
CONC. (In mg/Nm3)
|  |  | MAX. | MIN.
CDU/VDU | FF-01/02 | SO2 | 389.99 | 62.38 | 525 | Stack with dual firing (FG:FO=71:29)
|  | NOX | 132.23 | 11.43 | 379
|  | CO (FFI&II) | 8.69 | 2.75 | 164
DCU | FF-01 | SO2 | 254.25 | 11.7 | 756 | Stack with dual firing (FG:FO=57:43)
|  | NOX | 236.55 | 49.68 | 393
HCU | FF-01/02 | SO2 | 19.54 | 3.14 | 50 | Stack with Gas firing
|  | NOX | 35.56 | 12.13 | 350
HCU | FF-03 | SO2 | 203.25 | 13.77 | 216 | Stack with dual firing (FG:FO=90:10)
|  | NOX | 112.3 | 6.61 | 360
H2U | FF-01 | SO2 | 48.8 | 16.61 | 50 | Stack with Gas firing
|  | NOX | 44.02 | 16.22 | 350
MSP | FF-01 | SO2 | 39.84 | 16.56 | 50 | Stack with Gas firing
|  | NOX | 90.13 | 4.8 | 350
CPP HRSG |  | SO2 | 41.47 | 9.16 | 50 | Stack with dual firing (FG:NAP=100:00)
|  | NOX | 35.52 | 1.27 | 350
CPP UTILITY BOILER |  | SO2 | 46.83 | 10.14 | 50 | Stack with Dual firing (FG:FO=100:0)
|  | NOX | 112.9 | 6.57 | 350
DHDT |  | SO2 | 12.3 | 3.49 | 50 | Stack with Gas firing
|  | NOX | 27.5 | 7.8 | 350
* Limiting concentration of emission calculated as per MOEF new notification on standard vide GSR- 186 (E) dated 18th March, 2008. Emission level for all the stacks are found to be within limit

## ENV TABLE IV
NUMALIGARH REFINERY LIMITED
QUARTERLY PERFORMANCE WITH RESPECT TO ENVIRONMENTAL ASPECTS
DURING QUARTER I (APRIL-JUNE 21), 2021-22
Ambient Air Quality Data
STATION | PARAMETER | STD | Unit | OBSERVATIONS
|  | NAAQS-2009 |  | MAX | MIN | AVG
REFINERY (WATCH TOWER NO. 6) | SO2 | 80 (24 hr avg.) | μg/m3 | 14.1 | 8.1 | 11.12
| NO2 | 80 (24 hr avg.) | μg/m3 | 19 | 10.2 | 14.6
| O3 | 100 (8 hr avg.) | μg/m3 | 36.6 | 13.7 | 24.0533
| CO | 2.000 (8 hr.avg.) | mg/m3 | 1.04 | 0.52 | 0.88
| NH3 | 400 (24 hr.avg.) | μg/m3 | 33.8 | 15.7 | 24.18
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 65.5 | 38.1 | 53.1967
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 33.9 | 17.8 | 25.34
| Benzene | 05 (Annual) | μg/m3 | 3.1 | 1.5 | 2.38
| HC |  | mg/m3 | 1.21 | 0.56 | 0.90333
| BaP | 01 (Annual) | ng/m3 | <0.5 | <0.5 | <0.5
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.41 | 0.14 | 0.28667
| As | 06 (Annual) | ng/m3 | 1 | 1 | 1
| Ni | 20 (Annual) | ng/m3 | 4.1 | 1.3 | 2.44
ECO-PARK IN NRL TOWNSHIP | SO2 | 80 (24 hr avg.) | μg/m3 | 13.4 | 8.4 | 10.55
| NO2 | 80 (24 hr avg.) | μg/m3 | 18.6 | 11 | 13.9433
| O3 | 100 (8 hr avg.) | μg/m3 | 33.8 | 12.5 | 21.7867
| CO | 2.000 (8 hr.avg.) | mg/m3 | 0.97 | 0.54 | 0.75
| NH3 | 400 (24 hr.avg.) | μg/m3 | 32.5 | 12.5 | 21.3133
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 61.1 | 36.9 | 49.2333
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 33 | 14.8 | 23.02
| Benzene | 05 (Annual) | μg/m3 | 3.1 | 0.9 | 1.95
| HC |  | mg/m3 | 1.51 | 0.55 | 0.85333
| BaP | 1.0 (Annual) | ng/m3 | <0.5 | <0.5 | <0.5
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.38 | 0.17 | 0.26
| As | 6.0 (Annual) | ng/m3 | 1 | 1 | 1
| Ni | 20 (Annual) | ng/m3 | 3.9 | 1.2 | 2.4433
RAW WATER INTAKE | SO2 | 80 (24 hr avg.) | μg/m3 | 12.7 | 7.6 | 9.5767
| NO2 | 80 (24 hr avg.) | μg/m3 | 17 | 9.3 | 12.6467
| O3 | 100 (8 hr avg.) | μg/m3 | 34.1 | 14.5 | 22.7067
| CO | 2.000 (8 hr.avg.) | mg/m3 | 0.84 | 0.57 | 0.71333
| NH3 | 400 (24 hr.avg.) | μg/m3 | 29.2 | 12.8 | 21.6633
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 88.2 | 36.3 | 47.7733
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 28.6 | 13.5 | 21.6867
| Benzene | 05 (Annual) | μg/m3 | 3.2 | 0.9 | 1.95
| HC |  | mg/m3 | 1.1 | 0.56 | 0.80333
| BaP | 01 (Annual) | ng/m3 | <0.5 | <0.5 | <0.5
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.38 | 0.14 | 0.26
| As | 06 (Annual) | ng/m3 | 1 | 1 | 1
| Ni | 20 (Annual) | ng/m3 | 3.7 | 1.4 | 2.1467
NH-39 BYPASS | SO2 | 80 (24 hr avg.) | μg/m3 | 16 | 8.7 | 12.48
| NO2 | 80 (24 hr avg.) | μg/m3 | 21.9 | 10.9 | 16.5233
| O3 | 100 (8 hr avg.) | μg/m3 | 45.1 | 18.1 | 30.36
| CO | 2.000 (8 hr.avg.) | mg/m3 | 1.18 | 0.66 | 0.97
| NH3 | 400 (24 hr.avg.) | μg/m3 | 40.1 | 16.1 | 28.5833
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 74.1 | 43.6 | 60.3433
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 39.9 | 20.8 | 27.7467
| Benzene | 05 (Annual) | μg/m3 | 4 | 1.5 | 2.56
| HC | - | mg/m3 | 1.39 | 0.64 | 1.0667
| BaP | 1 | ng/m3 | <0.5 | <0.5 | <0.5
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.5 | 0.17 | 0.33667
| As | 6 | ng/m3 | 1 | 1 | 1
| Ni | 20 (Annual) | ng/m3 | 4.6 | 1.3 | 3.06
KAZIRANGA WILDLIFE SANCTUARY AT AGARTOLI | SO2 | 80 (24 hr avg.) | μg/m3 | 12 | 6.7 | 9.6167
| NO2 | 80 (24 hr avg.) | μg/m3 | 15.7 | 8.4 | 12.5833
| O3 | 100 (8 hr avg.) | μg/m3 | 31.9 | 14.4 | 20.6367
| CO | 2.000 (8 hr.avg.) | mg/m3 | 0.84 | 0.48 | 0.65333
| NH3 | 400 (24 hr.avg.) | μg/m3 | 28.3 | 10.9 | 19.51
| PM 10 | 100 (24 hr.avg.) | μg/m3 | 54 | 32.6 | 43.0567
| PM 2.5 | 60 (24 hr.avg.) | μg/m3 | 25.6 | 11.7 | 19.96
| Benzene | 05 (Annual) | μg/m3 | 2.9 | 0.9 | 2.0067
| HC | - | mg/m3 | 0.52 | 0.22 | 0.74667
| BaP | 1 | ng/m3 | <0.5 | <0.5 | <0.5
| Pb | 1.0 (24 hr.avg.) | μg/m3 | 0.37 | 0.13 | 0.23667
| As | 6 | ng/m3 | 1 | 1 | 1
| Ni | 20 (Annual) | ng/m3 | 3.4 | 1.1 | 2.2333
BDL:Below Detection Level, All the parameters are found to be within limt